| Current carrying capacity of the wires and cables with PVC insulation* |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal cross-section of conductors, mm2 | Current, А |  |  |  |  |  |  |  |  |  |  |  |
|  | external |  | In ducts |  |  |  |  |  |  |  |  |  |
|  | Copper conductors | Aluminium conductors | With copper conductors |  |  |  |  | With aluminium conductors |  |  |  |  |
|  |  |  | 2 single conductor | 3 single conductor | 4 single conductor | 1 twin conductor | 1 triple conductor | 2 single conductor | 3 single conductor | 4 single conductor | 1 twin conductor | 1 triple conductor |
| 0.5 | 11 | - | - | - | - | - | - | - | - | - | - | - |
| 0.75 | 15 | - | - | - | - | - | - | - | - | - | - | - |
| 1 | 17 | - | 16 | 15 | 14 | 15 | 14 | - | - | - | - | - |
| 1.2 | 20 | 18 | 18 | 16 | 15 | 16 | 14.5 | - | - | - | - | - |
| 1.5 | 23 | - | 19 | 17 | 16 | 18 | 15 | - | - | - | - | - |
| 2 | 26 | 21 | 24 | 22 | 20 | 23 | 19 | 19 | 18 | 15 | 17 | 14 |
| 2.5 | 30 | 24 | 27 | 25 | 25 | 25 | 21 | 20 | 19 | 19 | 19 | 16 |
| 3 | 34 | 27 | 32 | 28 | 26 | 28 | 24 | 24 | 22 | 21 | 22 | 18 |
| 4 | 41 | 32 | 38 | 35 | 30 | 32 | 27 | 28 | 28 | 23 | 25 | 21 |
| 5 | 46 | 36 | 42 | 39 | 34 | 37 | 31 | 32 | 30 | 27 | 28 | 24 |
| 6 | 50 | 39 | 46 | 42 | 40 | 40 | 34 | 36 | 32 | 30 | 31 | 26 |
| 8 | 62 | 46 | 54 | 51 | 46 | 48 | 43 | 43 | 40 | 37 | 38 | 32 |
| 10 | 80 | 60 | 70 | 60 | 50 | 55 | 50 | 50 | 47 | 39 | 42 | 38 |
| 16 | 100 | 75 | 85 | 80 | 75 | 80 | 80 | 80 | 60 | 55 | 60 | 55 |
| 25 | 140 | 105 | 115 | 100 | 90 | 100 | 100 | 85 | 80 | 70 | 75 | 65 |
| 35 | 170 | 130 | 135 | 125 | 115 | 125 | 135 | 100 | 95 | 85 | 95 | 75 |
| 50 | 215 | 165 | 185 | 170 | 150 | 160 | 175 | 140 | 130 | 120 | 125 | 105 |
| 70 | 270 | 210 | 225 | 210 | 185 | 195 | 215 | 175 | 165 | 140 | 150 | 135 |
| 95 | 330 | 255 | 275 | 255 | 225 | 245 | 250 | 215 | 200 | 175 | 190 | 165 |
| 120 | 385 | 295 | 315 | 290 | 260 | 295 | - | 245 | 220 | 200 | 230 | 190 |
| 150 | 440 | 340 | 360 | 330 | - | - | - | 275 | 255 | - | - | - |
| 185 | 510 | 390 | - | - | - | - | - | - | - | - | - | - |
| 240 | 605 | 465 | - | - | - | - | - | - | - | - | - | - |

* - Cables, wires and cords; (directory) / Belorussov N.I., Saakyan A.Е.,  Yakovleva А.I., М.: Energoatomizdat, 1988. - 510 p.

** - Conformity of cable products made according to GOST and QR to foreign standards is approximately.